## Site Screen
Site |  |  |  | Parcel (Regrid via Mireye) | [6 empty] | Power | [12 empty] | Gas / BTM | [5 empty] | Flood & Hazard | [10 empty] | Climate / Cooling |  |  |  | Air & Environment | [8 empty] | Water / Sewer | [6 empty] | Connectivity |  | Neighbors |  |  |  |  | Summary
Site | Lat | Lng | Screen depth | Situs address | Owner of record | APN | Zoning | Parcel area (m2) | Parcel area (acres) | Parcel caveat | ISO/RTO | Serving utility (retail) | Ind. elec price ($/kWh) | Est. annual cost ($/MW-yr) | Substation dist (m) | Substation max kV | Trans line dist (m) | Trans line kV | Trans line owner | Max kV within 10 km | Substations in 10 km | Redundancy flag | County queue (MW, generator-side) | Gas pipeline dist (m) | Interstate pipeline (m) | Ind. gas ($/MCF) | Grid ($/MWh) | Modeled gas gen ($/MWh, fuel-only) | BTM gas flag | FEMA zone | In SFHA | Seismic design cat. | PGA 2%/50yr (g) | Design wind (mph) | Karst | Nearest dam (m) | Dam hazard class | High-hazard dams 10 km | Shrink-swell | Slope (deg) | Design wet bulb (degC) | Days >=32C /yr | Free cooling h/yr @15C | Free cooling h/yr @10C | Ozone nonattainment | Worst class | Maintenance area | Superfund in 8 km | Brownfields in 8 km | USTs in 1 km | Open LUST in 1 km | Opportunity Zone | Incentive stack | In water service area | Water system | System pop served | In sewer service area | Sewer provider | WWTP dist (m) | WWTP pop served | FTTP providers | 5G class | Housing units 1 km | Density (units/km2) | Residential context | School dist (m) | School name | Rank | Key strengths | Key risks | Verdict | Recommendation
Ashland, Boyd Co KY | 38.4758 | -82.6439 | Full (greenfield recipe - predates conversion recipe; no building/conversion fields) | not pulled | not pulled | not pulled | R-5 | 4388.49 |  | Single-point Regrid match - FRAGMENT RISK: R-5/1.08-ac may be adjacent lot if site is a multi-parcel assemblage (Northfield pattern); county check needed | not pulled | Kentucky Power Co | 0.073 | 639480 | 1446.8 | 69 | 695.8 | 69 | Kentucky Power Co | 69 | 15 | TRUE | absent | 6713.6 | 6713.6 | 4.51 | 73 | 41.32 | TRUE | X | No | B | 0.135 | 112 | No | 9078.4 | High | 2 | Low | 1.21 | 25 | 28 | 4531 | 3434 | No | absent | No | 10 | 21 | 34 | 0 | No | (none) | Yes | Ashland Water Works | 44402 | Yes | Ashland | 1771 | 21481 | 2 | 5g_high_speed | 1735 | 381.1 | dense | 221 | Ashland Child Development Center | 9 | Operating facility (established use); Zone X; flat; water+sewer in-area; best OH-valley gas economics ($41 vs $73 grid); 345 kV substation 6.6 km | 69 kV ceiling in radius caps ~5-15 MW; expansion friction from dense residential + childcare 221 m; parcel zoning/size unverified (fragment risk); greenfield-recipe screen only | REVIEW (5-15 MW band) | Keep as low-band expansion candidate; re-screen with conversion recipe + county assemblage check after Sept 1
Baldwin GA - 2000 Communications Blvd | 34.4972 | -83.55 | Full (conversion screen) | 2000 COMMUNICATIONS BLVD | absent | 090 016 | HI | 106647.29 |  | Validated: coord + address pulls returned same parcel; address exact match | absent | Georgia Power Co | 0.0684 | 599184 | 1300.6 | 115 | 169.5 | 115 | Georgia Power Co | 115 | 10 | TRUE | absent | absent | 51825.7 | 5.56 | 68.4 | 50.94 | absent | X | No | C | 0.195 | 112 | No | 3629.9 | Low | 3 | Low | 0.35 | 24.5 | 24 | 4154 | 2717 | No | absent | No | 0 | 2 | 1 | 0 | No | (none) | No (54 m to boundary) | absent | absent | Yes | Baldwin WPCP | 2067 | 5231 | 1 | 5g_high_speed | 778 | 136.4 | dense | 1249 | Baldwin Elementary School | 1 | Operating facility + 26.35-ac HI parcel for expansion; 115 kV line 170 m; attainment air; clean environmental radius; full 5-50 MW band | No gas fallback (interstate 52 km); outside water area (54 m extension); small WWTP (5,231); no queue visibility (non-RTO) | GO | Pursue first - open Georgia Power capacity inquiry now
Northfield OH - 54 Leonard Ave | 41.3147 | -81.537 | Full (conversion screen) | LEONARD AVE | Kinetic ABS OH LLC | 4002466 | T-C | 463.24 |  | FRAGMENT - wrong parcel for address; county shows 7-parcel assemblage (APNs 4002461-4002467); building on 4002461 | PJM | City of Cleveland (OH) - SUSPECT | 0.0995 | 871620 | 1090.9 | absent | 893.1 | 345 | absent | 345 | 23 | TRUE | absent | 534.6 | 24864.2 | 11.23 | 99.5 | 102.88 | TRUE | X | No | B | 0.095 | 112 | No | 1699.4 | High | 3 | Low | 3.77 | 24.1 | 8 | 5538 | 4258 | Yes - ozone (2015 std) | Serious | Yes (2008 ozone) | 7 | 2 | 4 | 2 | No | (none) | Yes | Cleveland Public Water System | 1308955 | Yes | NEORSD Southerly WWTP | 7099 | 21809 | 4 | 5g_high_speed | 1137 | 196.8 | dense | 87 | Nordonia Middle School | 3 | Operating facility (established use beside school); best wires in portfolio - 345 kV line 893 m, 23 substations/10 km; 1.3M-person water system; 4 fiber providers; strong cooling | Serious ozone (incremental genset permitting, netting possible vs existing permits); $872k/MW-yr power; parcel data unreliable (7-parcel assemblage); utility attribution suspect; nearest UST 30 m likely own fuel tank | REVIEW | Rises under operating-facility lens - verify serving utility (FirstEnergy?) + assemblage, then utility capacity inquiry on the 345 kV path
Hudson OH - 1300 Terex Rd | 41.2171 | -81.4425 | Full (conversion screen) | 1300 TEREX RD | Kinetic ABS OH LLC | 3003811 | DISTRICT-8 | 3254.56 |  | Single matched parcel; owner holds 16 Summit Co parcels - may be part of assemblage | PJM | City of Hudson (OH) - verified real muni | 0.0995 | 871620 | 1054.1 | 138 | 814.1 | absent | absent | 138 | 21 | TRUE | absent | 724 | 30645.3 | 11.23 | 99.5 | 102.88 | TRUE | X | No | B | 0.085 | 112 | No | 2007.5 | Significant | 5 | Low | 1.29 | 24 | 8 | 5448 | 4240 | Yes - ozone (2015 std) | Serious | Yes (2008 ozone) | 1 | 3 | 3 | 0 | No | (none) | Yes | Hudson City PWS | 8385 | No (546 m to boundary) | absent | 6095 | 16758 | 4 | 5g_high_speed | 944 | 86.3 | dense | 256 | The Goddard School | 4 | Operating facility; 138 kV substation 1.1 km; 21 substations/10 km; clean environmental; strong cooling; 4 fiber providers | Municipal utility counterparty at 50 MW; Serious ozone (incremental gensets need Tier 4); outside sewer area; small water system | REVIEW | Advance - gauge Hudson Public Power capacity appetite for the increment; spec Tier 4 gensets
Newark OH - 66 N 4th St | 40.0594 | -82.4049 | Full (conversion screen) | 66 N 4 ST | Kinetic ABS OH LLC | 02121190402004058000 | DC | 1113.45 |  | Single matched parcel; downtown CBD - possible assemblage | PJM | Ohio Power Co (AEP) | 0.0995 | 871620 | 928.1 | absent | 605.7 | 69 | Ohio Power Co | 69 | 21 | TRUE | 710.04 | 2707.6 | 2707.6 | 11.23 | 99.5 | 102.88 | TRUE | X | No | B | 0.085 | 112 | No | 3160.8 | Significant | 0 | Low | 0.84 | 24.6 | 11 | 5045 | 3940 | No | absent | Yes (2008+2015 ozone) | 5 | 16 | 16 | 1 | No | brownfield_repowering_screened | Yes | Newark City PWS | 49934 | Yes | Newark WWTP & Sewer System | 2889 | 10538 | 3 | 5g_high_speed | 3135 | 541.4 | dense | 182 | Child Of God Preschool | 8 | Operating facility (established downtown use); solid AEP counterparty; maintenance-only air (best air status in the OH group); water+sewer in-area; 710 MW county queue | 69 kV ceiling in entire radius caps ~5-15 MW; nearest UST 33 m likely own tank but 16 USTs/16 brownfields in downtown radius (diligence); expansion friction from preschool 182 m + density | REVIEW (5-15 MW band) | Keep as low-band expansion candidate - AEP capacity inquiry decides it
Riverside TX - FM 980 (Walker Co) | 30.8515 | -95.4001 | Full (conversion screen) | FM 980 | Valor Telecommunications of Texas LP | 14123 | absent | 2327.99 |  | Single matched parcel; rural - assemblage unknown | ERCOT (field) - SUSPECT, wires are Entergy TX (likely MISO) | Mid-South Electric Coop Assn | 0.0633 | 554508 | 1467.8 | 138 | 802.7 | 69 | Entergy Texas, Inc. | 138 | 2 | FALSE | 150 | 544.7 | 544.7 | 3.12 | 63.3 | 28.58 | TRUE | A | YES - SFHA, no BFE published | B | 0.045 | 112 | No | 1640 | Low | 2 | Low | 0.85 | 26.2 | 104 | 2693 | 1460 | No | absent | No | 0 | 0 | 2 | 0 | No | (none) | Yes | Riverside SUD | 6492 | No (7,460 m to boundary) | absent | 10865 | 3010 | 1 | 5g_high_speed | 315 | 32.2 | moderate | 9750 | (unreliable Overture record) | 10 | Operating facility already living with the flood zone; cheapest grid ($555k/MW-yr); best usable gas hedge ($29 vs $63, pipeline 545 m, attainment air); 138 kV | FEMA Zone A (no BFE) - substantial-improvement rule bites densification capex >50% of building value regardless of existing ops; worst-tier cooling; 2 substations/10 km, redundancy FALSE; sewer 7.5 km | NO-GO (flood) | Park - spend ~$2k on elevation certificate; revive only if LOMA path viable
Harrison AR - 202 Graham St | 36.2143 | -93.0791 | Full (conversion screen) | 202 GRAHAM STRE | absent | 825-14426-200 | C3 | 40473.46 |  | Single matched parcel - 10.0 ac; only multi-acre parcel besides Baldwin | MISO | Entergy Arkansas LLC | 0.062 | 543120 | 960.6 | 161 | 960.6 | 161 | Entergy Arkansas Inc | 161 | 3 | TRUE | absent | 5124.3 | 62989.5 | 9.28 | 62 | 85.01 | TRUE (flag only - see risks) | X | No | D | 0.225 | 112 | YES - carbonate, EXPOSED (Boone Fm) | absent | absent | 0 | absent | 2.58 | 25.6 | 38 | 4294 | 2981 | No | absent | No | 0 | 0 | 3 | 0 | No | (none) | Yes | Harrison Waterworks | 17455 | Yes | Harrison WWTP | 2947 | 13468 | 3 | 5g_high_speed | 388 | 38.4 | moderate | 1158 | Educational Opportunity Center | 2 | Operating facility + 10.0-ac C3 parcel for expansion; 161 kV substation+line ~960 m; cheapest power in portfolio ($543k/MW-yr); attainment; spotless environmental | Exposed carbonate karst + seismic design cat. D - governs NEW expansion structures (existing building's decades of service partly de-risk); only 3 substations/10 km; gas gen uneconomic | GO (leaning) | Pursue #2 - geotech karst study for expansion footprint + Entergy capacity inquiry in parallel
Moultrie GA - 216 4th St SE | 31.1775 | -83.7837 | Full (conversion screen) | 216 4TH ST SE | absent | M035 001 | C-3 | 5286.65 |  | Single matched parcel - 1.31 ac | absent | City of Moultrie (GA) - muni | 0.0684 | 599184 | 565.6 | 115 | 302.9 | 115 | Georgia Power Co | 115 | 15 | TRUE | 130 | 4850.7 | 4850.7 | 5.56 | 68.4 | 50.94 | TRUE | X | No | B | 0.065 | 112 | Buried carbonate (low confidence) | 2624.8 | Low | 1 | Low | 0.94 | 26.4 | 69 | 2658 | 1372 | No | absent | No | 0 | 2 | 32 | 2 | YES - tract 13071970702 | opportunity_zone | Yes | Moultrie | 17067 | Yes | Moultrie WPCP | 2852 | 13760 | 1 | 5g_high_speed | 1285 | 188.2 | dense | 775 | Stringfellow Elementary School | 5 | Operating facility; only Opportunity Zone site (capital-stack sweetener); 115 kV line 303 m (GA Power wires); attainment; 15 substations/10 km | Muni retail counterparty; nearest UST 31 m likely own tank but 32 USTs + 2 open LUST in 1 km (Phase I); hot climate (69 days >=32C); 1.31-ac parcel | REVIEW | Hold as OZ-advantaged backup; Phase I environmental if advanced
Newton IA - 115 S 2nd Ave W | 41.6983 | -93.0545 | Full (conversion screen) | 115 S 2ND AVE W | CSL Iowa System LLC (Uniti leaseback) | 0834158001 | C-CBD | 1731 |  | Single matched parcel; downtown CBD - possible assemblage | MISO | Consumers Energy - SUSPECT (likely Alliant/IPL; a Consumers Energy Coop exists in IA) | 0.0626 | 548376 | 784.2 | 161 | 751.7 | absent | MidAmerican Energy Co | 161 | 4 | TRUE | absent | 4438.6 | 4438.6 | 6.69 | 62.6 | 61.29 | TRUE | X | No | B | 0.045 | 112 | No | 2844.3 | Low | 0 | Moderate | 2.88 | 26.7 | 16 | 5312 | 4331 | No | absent | No | 1 | 0 | 23 | 2 | No | brownfield_repowering_screened | Yes | Newton Water Supply | 16518 | Yes | Newton WWTP | 274 | 16283 | 3 | 5g_high_speed | 2685 | 494.5 | dense | 426 | Central Junior High School | 6 | Operating facility; 161 kV substation 784 m; cheap power ($548k/MW-yr); attainment; excellent cooling (5,312 h) | 0.43-ac CBD fragment (assemblage unknown); Uniti (CSL) leaseback ownership - counterparty differs; utility attribution suspect; superfund 827 m + 2 open LUST (diligence); expansion friction from junior high 426 m | REVIEW | Hold - verify Alliant service, assemblage, and Uniti lease terms; mid-tier
Sugar Land TX - Fort Bend Co | 29.6363 | -95.5982 | TRIAGE ONLY (credits) - no parcel/building/school | not pulled | not pulled | not pulled | not pulled | not pulled | not pulled | Parcel fields not pulled - credit exhaustion; complete after Sept 1 reset | ERCOT (eGRID ERCT) | CenterPoint Energy (wires; retail via competitive REP) | 0.0633 | 554508 | 913.6 | 138 | not pulled | not pulled | not pulled | not pulled | 18 | TRUE | 3320.46 | 615.1 | 726.7 | 3.12 | 63.3 | 28.58 | TRUE | X | No | A | 0.045 | 136 | No | 3892.1 | High | 1 | VERY HIGH | 1.37 | 27.1 | 106 | 1994 | 1032 | Yes - ozone (2008+2015 stds) | SEVERE | No | 1 | 2 | 5 | 0 | No | brownfield_repowering_screened | Yes | City of Sugar Land | 90909 | Yes | Sugar Land North WWTP | 2299 | 1239 | 4 | 5g_high_speed | 1677 | 296.4 | dense | not pulled | not pulled | 7 | Operating facility; Zone X despite Houston metro; 18 substations/10 km; 3.3 GW county queue (hot market); best gas economics on paper; nearest UST 29 m likely own tank | SEVERE ozone (25 tpy NOx major threshold - neutralizes gas play, forces Tier 4 on incremental gensets); 136 mph design wind; very-high shrink-swell clays; worst cooling (1,994 h); screen incomplete | REVIEW (incomplete) | Complete parcel screen after Sept 1 credit reset before judging

## Notes & Caveats
TBDI x Mireye site screen - data notes
Session | All values pulled via mireye-earth MCP on 2026-08-11. Sources per field: FEMA NFHL, EIA Power Atlas, Regrid, EPA (Green Book/FRS/UST Finder/Sewersheds/CWS/CWNS), LBNL Queued Up, NREL NSRDB, NOAA/ASCE, USGS (NSHM/karst/3DEP/landslide), USACE NID, Census TIGERweb, FCC BDC, Overture.
OPERATING-FACILITY LENS | Per Tucker (2026-08-11): all candidate sites are already OPERATING data centers/telecom facilities. Verdicts are therefore scored as brownfield capacity EXPANSION, not new-use siting: school/residential-density findings are expansion friction (noise, construction, incremental permits), NOT use-permission knockouts - the existing use is established/grandfathered. Zoning of record (e.g. R-5 at Ashland, T-C at Northfield) likewise does not block an existing use, only complicates expansion. What the lens does NOT change: wires (voltage ceilings cap the MW band), flood (substantial-improvement rule still bites densification capex), climate/cooling, geology, and counterparty structure.
Nearest-UST pattern | Nearest UST distances of ~29-33 m at Northfield, Newark, Moultrie and Sugar Land are most plausibly the facilities' OWN registered backup-fuel tanks - normal operating infrastructure, not third-party contamination risk. Wider-radius UST/brownfield/LUST counts remain genuine diligence items.
'absent' vs 'not pulled' | 'absent' = the source confirmed no data exists there (a real answer, e.g. no dam within 10 km). 'not pulled' = field was never requested (Boyd test screen used a different recipe; Sugar Land hit the monthly credit ceiling).
Parcel areas are FLOORS, not site sizes | Regrid returns the single parcel under the query point. Telecom exchanges are frequently multi-parcel assemblages: at Northfield OH, county records show a 7-parcel site and Mireye returned a 0.11-ac vacant fragment twice (coordinate AND rooftop-geocoded address), with every quality flag clean. Treat every small parcel value as a fragment until county records confirm. Only Baldwin GA was cross-validated (two independent pulls returned the identical 26.35-ac parcel).
Serving-utility field | Retail biller only - never the transmission owner or interconnection counterparty. Two values look wrong (overlapping-territory polygon errors): Northfield 'City of Cleveland' (expected FirstEnergy/Ohio Edison) and Newton 'Consumers Energy' (expected Alliant/IPL; note a real Consumers Energy Coop exists in Iowa). Verify against the site's actual power invoices.
County queue (MW) | LBNL Queued Up tracks GENERATOR interconnection queues. Read as grid congestion / market-activity signal, never as capacity available to serve load.
Deliverable MW | Not derivable from these fields. Feeder/transformer headroom requires a utility capacity study per site (contract-gated Mireye power-band product also exists).
Ozone nonattainment at 5-50 MW grid-primary | Constraint on the backup genset fleet, not the grid draw. Major-source NOx thresholds: 100 tpy attainment / 50 tpy Serious / 25 tpy Severe. ~5 MW fleets are minor everywhere; ~50 MW fleets in Serious/Severe areas need Tier 4/SCR engines + capped test hours (~15-25% genset capex premium, longer permitting). Severe status also forecloses non-emergency running - it neutralizes Sugar Land's behind-the-meter gas advantage.
Building fields (Overture) | Excluded as unreliable: footprint was ~10x off at Northfield vs. owner records; class/floor labels missing at most sites. Use owner-provided interior square footage instead.
Riverside TX flood | Zone A = SFHA mapped by approximate methods, NO base flood elevation published. Substantial-improvement rule likely triggered by any conversion. Cheapest resolution: elevation certificate + LOMA attempt (~$1-3k) before any further spend.
MW band rule of thumb | 69 kV network: low tens of MW where headroom exists. 115-161 kV: comfortably covers 50 MW. 345 kV tap: only pencils at the very top of the range.
Ownership pattern | Sites sit in different Windstream entities: Kinetic ABS OH LLC (OH sites, ABS vehicle, Dec 2025 transfers), CSL Iowa System LLC (Uniti leaseback), Valor Telecommunications of Texas LP. Negotiating counterparty differs by site.
Credit state | Free plan 5,000/mo effectively exhausted (~4,999 used); resets 2026-09-01. Outstanding: Sugar Land parcel/school fields (~310 credits). Session total ~5,000 credits across 10 screens (screens ran ~450 each after recipe was tuned; early Boyd screen + missteps cost more).
Verdicts | GO = advance to diligence now. REVIEW = real candidate with named blockers to resolve first. REVIEW (5-15 MW band) = viable only at the low end of the 5-50 MW target due to 69 kV wires. NO-GO = disqualified on current facts. Under the operating-facility lens the only siting NO-GO left is Riverside's floodplain - the portfolio is otherwise a power-expansion ranking (wires x yard space x permitting increment).
Rank | 1 Baldwin GA, 2 Harrison AR, 3 Northfield OH (rises on 345 kV once school objection reframed), 4 Hudson OH, 5 Moultrie GA, 6 Newton IA, 7 Sugar Land TX (incomplete), 8 Newark OH (5-15 MW band), 9 Ashland KY (5-15 MW band; greenfield-recipe screen only, parcel fragment risk), 10 Riverside TX (flood; potentially resolvable via ~$2k elevation certificate/LOMA).